Site Safety Plan Guidelines


1 - Purpose: Prevent the occurrence of injury or loss of property due to the actions or omissions of the General Contractor and or Sub-Contractors who may be engaged in portions of project. In addition, this Fire Protection plan is intended to gain compliance with all requirements of New York State Fire Code Chapter 33 “Fire Safety During Construction and Demolition”.


2 - Project Title and Location:  __________________________________________


3 - Building Owner: ___________________________________________________

   - Building Occupant: 

Contact:   ______________________	Phone:  ___________________


3 - Project Manager:  

Contact:   ______________________	Phone:  ___________________


4 - General Contractor: 

 Contact:   ______________________	Phone:  ___________________


5 – Site Safety Director:  

  Contact:   ______________________	Phone:  ___________________
   

6 - Fire Chief: UB Fire & Life Safety Manager will serve in this capacity, coordinating with the fire response agency having jurisdiction.


7 - Code Enforcement Official:  UB Fire & Life Safety Manager will function as the Fire Code Enforcement Official.


8 – EMERGENCY PROCEDURE:  FIRE or MEDICAL EMERGENCY 

Notify the University Police Dispatcher Immediately
By Dialing 716-645-2222
9 - Program:  

The General Contractor shall be responsible for maintaining compliance with this plan on the job site.  All General Contractor and Sub-Contractor employees will comply with the requirements of this Site Safety Plan and NYS Codes.

The Site Safety Director shall be responsible for ensuring that the Site Safety Plan is carried out through completion of the project.  

3303.1.1 Components of Site Safety Plan.  Include the following as applicable:

1. Name and contact information of site safety director.
2. Documentation of the training oof the site safety director and fire watch personnel.
3. Procedures for reporting emergencies.
4. Fire department vehicle access routes.
5. Location of fire protection equipment, including portable fire extinguishers, standpipes, fire department connections and fire hydrants.
6. Smoking and cooking policies.
7. Location and safety considerations for temporary heating equipment.
8. Hot work permit plan.
9. Plans for control of combustible waste material.
10. Locations and methods for storage and use of flammable and combustible liquids and other hazardous materials.
11. Provisions for site security and where required, for a afire watch.
12. Changes that affect this plan.
13. Other site-specific information required by the fire code official.


10 - Temporary Heating Equipment: Fire Code Section 3305

3305.1 Temporary heating devices shall be Listed and Labeled in accordance with the Mechanical Code or the Fuel Gas Code of New York State.  Installation, maintenance and use of temporary heating devices shall be in accordance with the terms of the listing.

3305.1.1 Oil Fired Heaters shall comply with Section 605

3305.1.2 LP gas fired heaters shall comply with Chapter 61 Fuel Gas Code of New York State 

3305.1.3 Refueling operations shall be conducted in accordance with Section 5705.  The appliance shall be allowed to be cool prior to refueling.

3305.1.4 Clearance to combustibles from temporary heating devices shall be maintained in accordance with the labeled equipment.  When in operation, temporary heating devices shall be fixed in place and protected from damage, dislodgement or overturning in accordance with the manufacturer’s instructions.

3305.1.5 Use of temporary heating devices shall be supervised and maintained only by competent personnel.


11 - Precautions Against Fire: Fire Code Sections 3303, 3304, and 3305

3304.1.1 Combustible waste materials, debris, rubbish and waste material shall not be accumulated within buildings.

3304.1.2 Combustible waste material, debris, rubbish and waste material shall be removed from buildings at the end of each shift of work.

3304.1.3 Rubbish containers with a capacity exceeding 5.33 cubic feet (40 gallons) are used for temporary storage of combustible debris, rubbish and waste material, they shall have tight-fitting or self-closing lids.  Such rubbish containers shall be constructed entirely of materials that comply with either of the following: Noncombustible materials or materials that meet a peak rate of heat release as detailed in NYS Fire Code.

3304.2 Materials susceptible to spontaneous ignition, such as oily rags, shall be stored in a listed disposal container.

3305.2 Per campus policy, smoking is prohibited while on campus.  No smoking signage shall be placed at the contractor’s entrance to the building or buildings, in the contractor’s trailers, at the job site entrance gate and in highly visible and obvious locations as may be prescribed by the University at Buffalo Fire & Life Safety Manager.    

3305.3 No burning of waste materials on site is permitted.

3303.5 Fire Watch.  Where required by the code enforcement official or the site safety plan established in accordance with Section 3303.1, a fire watch shall be provided for building demolition and for building construction. 

3305.5 Cutting and Welding.  Welding, cutting, open torches and other hot work operations and equipment shall comply with Chapter 35 or NYS Fire Code. 

3305.9 Hot Work Operations.  The site safety director shall ensure hot work operations and permit procedures are in accordance with Chapter 35 of NYS Fire Code and the University at Buffalo Hot Work Permit process.  Hot Work applications available at:  https://www.buffalo.edu/administrative-services/managing-facilities/environment-health-and-safety/working-safely/fire-life.html

3305.6 Temporary wiring for electrical power and lighting installations used in 
connection with the construction, alteration or demolition of buildings, structures,   equipment or similar activities shall comply with NFPA 70.

            All electrical tools and equipment used on site during construction, alteration 
            and or demolition shall be in good working order.  Frayed cords, broken 
            connectors, cords that have been tapped over and cords that are undersized for the 
            as used load, will not be allowed. 


12 - Flammable and Combustible Liquids:   Fire Code Section 3309

3309.1 Flammable and combustible liquids shall be stored in compliance with Section 5704 of the NYS Fire Code.    
 
3309.1.1 Storage use and handling of Class I and Class II flammable and combustible liquids shall be in accordance with Section 5706.2 of the NYS Fire Code.  Ventilation shall be provided for operations involving the application of materials containing flammable solvents.

3309.1.2 Housekeeping of flammable and combustible liquid storage areas shall be maintained clear of combustible vegetation and waste materials.  Such storage areas shall not be used for the storage of combustible materials.

3309.1.3 Precautions against fire.  Sources of ignition shall be prohibited in flammable and combustible liquid storage areas.  Signs shall be posted in accordance with Section 310 of the Fire Code.  

3309.1.4 Flammable and combustible liquids shall be kept in approved safety containers, clearly marked to indicate contents.

3309.1.5 Leakage or Spills shall be immediately reported to the University at Buffalo.  

Any hazardous materials spilled material shall be cleaned up as is required by New York State and Federal law.  University at Buffalo Facilities Environment Health & Safety shall be notified immediately in the event of any spill of flammable or combustible liquids on University at Buffalo property.


13 - Flammable gases: Fire Code Chapter 33, 35, 53, and 58

The storage, use and handling of flammable gases shall be in compliance with Chapter 33, 35, 53, and 58 of the Fire Code of New York State.  All related equipment, i.e. hoses, tips and regulators must be in good working condition.  Use of equipment appearing to be in less then good condition will not be allowed on University at Buffalo property.

All flammable compressed gas cylinders shall be secured.
All flammable compressed gas cylinders shall be stored in a remote location away from the immediate hot work and construction when not in use.


14 – Additional Safeguards:  Storage Fire Code Section 3310

3310.1 Storage.  Combustible materials associated with construction, demolition, remodeling or alterations to an occupied structure shall not be stored in exits, enclosures for stairways and ramps, or exit access corridors serving an occupant load of 30 or more.  Exceptions: Where the only occupants are construction workers and temporary accumulation to support work being performed when workers are present.


15 – Administrative Safety Controls:   Fire Code Section 3303

3303.1 Program Development and Maintenance:  Development, implementation and maintenance of an approved, written site safety plan establishing a fire prevention program at the project site applicable throughout all phases of the construction, repair, alteration or demolition work. The plan addresses the requirements of chapter 33 and other applicable portions of the NYS Fire Code, the duties of staff and staff training requirements. The plan shall be submitted and approved before a building permit is issued. Any changes to the plan shall be submitted for approval.

3303.2 Site Safety Director:  The site safety director shall be responsible for ensuring compliance with the site safety plan. The site safety director shall have the authority to enforce the provisions of chapter 33 and other provisions as necessary to secure the intent of this chapter. 

A pre-fire plan shall be developed by the Site Safety Director. The pre-fire plan shall be approved by the Fire Code Enforcement Official.  The Code Enforcement Official shall be notified of changes affecting the utilization of information contained in such pre-fire plans.   

In event of fire the designated contractor working on site shall take the following action:
· Rescue anyone who may be in immediate danger
· Activate the building fire alarm system
· Call or designate someone to call UB Police 716-645-2222
· Contain fire by isolating in a room or container
· Extinguish (if trained) using portable fire extinguisher


*University at Buffalo specific requirements for Emergencies for Asbestos Removal Projects                                                                    

*Asbestos Projects: Fire event within containment - The Contractors working in containment at the time a fire event occurs may use a portable fire extinguisher if the fire is small and has not spread beyond the object of origin.  They must then exit containment immediately and report the fire event to the University Police.  

*Fire Alarm System Activation - With no fire or smoke showing contractors shall exit containment and the building immediately and assemble with other building evacuees, the lead person shall report to University Police on conditions within containment.  In the event the fire alarm activation occurred within containment a qualified person, under the direction of the Fire Department will enter containment to confirm that no fire or smoke condition exists.   

3303.2.1 Training of responsible personnel in the use of fire protection equipment shall be the responsibility of the Site Safety Director. Documentation of this required training, indicating content and individual trainees shall be provided to the Fire Chief and the Code Enforcement Official. 

3303.3 Daily Fire Safety Inspection.  The site safety director shall be responsible for completion of a daily fire safety inspection at the project site. Each day, all building and outdoor areas shall be inspected to ensure compliance with the inspection list in this section. The results of each inspection shall be documented and maintained on-site until a certificate of occupancy has been issued. Documentation shall be immediately available on-site for presentation to the fire code official upon request.

Detailed list, Chapter 33, 3303.3, items 1 – 11.

3303.3 Emergency telephone.  Emergency telephone facilities with ready access shall be provided in an approved location at the construction site, or an approved equivalent means of communication shall be provided. 

A clearly legible instructional sign posted at the emergency telephone shall provide instructions for calling University Police at 716-645-2222 to report emergency events. The instructional sign shall include the location of the phone and construction or demolition site.

              
3306.2 Impairment of the fire detection/alarm system or a portion of the fire                  detection/alarm system shall be in accordance with Chapter 9 Section 901 of the Fire Code of New York State.  

Impairment of the fire detection/alarm system or portion of the fire detection/alarm system shall not be done unless the University at Buffalo Facilities Electrical Shop has advanced notice.  

Requests for fire alarm impairment can be made by calling 716-645-2025.

The Site Safety Director shall be responsible for notifying Building occupants of the status of the building fire detection/alarm and suppression systems, through written notice and the use of signage at the building entrances.  

3306.3 & 3306.4 Smoke Detectors and Smoke Alarms, Temporary Coverings.  Fire detection devices may be covered in-order to protect them from damage, exposure to water or dust during the demolition and or construction process. Coverings placed on or over fire protection devices shall be removed on completion of the project work in the area where the device is located.  

The designated contractor is responsible for protecting fire detection devices from damage or exposure to dust during the demolition and construction process and returning the system to full functionality at the end of each work period.

           In areas under asbestos abatement, coverings on fire detection devices may remain 
           while each area is in under containment and shall be removed from devices as 
           soon as abatement work is completed.     


16 – Fire Department Site Access and Water Supply:   Fire Code Section 3307

3307.1 Approved vehicle access for firefighting shall be provided to all construction or demolition sites. Vehicle access shall be provided to within 100 feet of temporary or permanent fire department connections. Vehicle access shall be provided by either temporary or permanent roads, capable of supporting vehicle loading under all weather conditions. Vehicle access shall be maintained until permanent fire apparatus access roads are available. 
        
           Asbestos containment areas shall be clearly marked at all access points to alert 
           fire department personnel of the need for personal protective equipment and  
           decontamination procedures in the event entry is necessary.

3307.2 An approved water supply for fire protection, either temporary or permanent, shall be made available as soon as combustible building materials arrive on the site, on commencement of vertical combustible construction and on installation of a standpipe system in buildings under construction, in accordance with sections 3307.1 through 3307.4


17 - Portable Fire Extinguishers:   Fire Code Section 3306.6

3306.6 Structures under construction, alteration or demolition shall be provided with not less than one approved portable fire extinguisher in accordance with Section 906 and sized for not less than ordinary hazard as follows:

1. At each stairway on all floor levels where combustible materials have accumulated.
2. In every storage and construction shed.
3. Additional portable fire extinguishers shall be provided where special hazards exist including, but not limited to, the storage and use of flammable and combustible liquids.

The Site Safety Director shall notify EH&S of portable fire extinguishers in areas affected by the demolition and or the construction process.  EH&S will remove those portable fire extinguishers prior to the start of work.    

The General Contractor shall be responsible for providing portable fire        extinguishers in the work areas under their control. 

The Site Safety Director shall notify EH&S when work areas are released back to the University so that University portable fire extinguishers may be returned. 




18 - Safeguarding Roofing Operations: Fire Code Section 3305.10

3305.10 Roofing operations utilizing heat-producing systems or other ignition sources shall be conducted in accordance with Sections 3305.10.1 and 3305.10.2 and Chapter 35.



Please provide detailed information about how the project will address applicable requirements of this document in your site safety plan.

This document provides an overview of select project details for work being conducted at the University at Buffalo.  Full review and compliance with all applicable NYS Fire Code chapters and sections remain the responsibility of the owner, the owner’s authorized agent and the Site Safety Director.







Reviewed and Accepted by _____________________________ 


By: 												
       Signature/Title							Date



Reviewed and Accepted by _____________________________


By: 												
       Signature/Title							Date



Reviewed and Accepted by Marjory Jaeger, Fire and Life Safety Manager, UB EH&S


By: 												
       Signature/Title							Date
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